## Slide 1
Weekly report: Electrical Drivetrain
Week number: 8
Date: 11/18/2025
Supervisor: Prof. Dr.-Ing. Saiju
Group members: Aiswarya Vijayan, Vishranti Shivajirao Patil , Girish Mahadeo Padalkar, Cristina Milene Vergara Hernandez

## Slide 2: List of contents
Cristina Vergara
Electrical Drive Train/ Optimus Syria
Implement MATLAB model of the DFIG
Generate characteristic curves (T–N, I–N, P–N)
Validate generator behavior across speed range
Begin building the Simscape model for all drivetrain components
Results for Converter Parameters

## Slide 3: Generator and Parameters
Cristina Vergara
Electrical Drive Train/ Optimus Syria
Parameter | Symbol | Value | Unit
Rated Active Power | Pn | 5.31e6 | W
Line Voltage (LL) | Vn | 960 | V
Frequency | f | 50 | Hz
Number of Poles | p | 6 | –
Pole Pairs | pp | 3 | –
Stator Resistance | Rs | 0.0818 | Ω
Rotor Resistance | Rr | 0.253 | Ω
Stator Leakage Inductance | Lls | 0.001474 | H
Rotor Leakage Inductance | Llr | 0.001474 | H
Magnetizing Inductance | Lm | 0.01295 | H
Rotor/Stator Volt. Ratio | Vr/Vs | 0.2 | –
Synchronous Speed | Ns | 1000 | rpm
Rated Rotor Speed | Nr | 1200 | rpm
Slip (supersync.) | s | –0.2 | –
Rotor Inertia | J | 4647 | kg·m²

## Slide 4: Torque-Speed Characteristic
Cristina Vergara
Torque is positive below synchronous speed
Zero torque ~1000 rpm
Negative torque above synchronous speed → generator region
Curve shape matches theoretical DFIG characteristics

## Slide 5: Stator Current vs Rotor Speed
Cristina Vergara
Stator current is lowest near synchronous speed
Higher slip → higher stator current
Symmetrical behaviour indicates correct model implementation

## Slide 6: Mechanical Power vs Rotor Speed
Cristina Vergara
Mechanical power peaks at low speed (motor side)
Zero crossing at synchronous speed
Becomes negative in generator range (expected)
Confirms correct energy flow direction

## Slide 7: Progress on Simscape Drivetrain Model
Cristina Vergara
DFIG block selected and configured
Parameters identified (R, L, Lm, poles, rated values)
Values transferred from design table into the model
Model runs with custom generator parameters

## Slide 8: Converter Parameters (Updated)
Cristina Vergara
Parameter | Unit | Value | Notes | 
Power Range | MW | 1.25 | 25% of 5MW DFIG | 
Nominal Voltage (VLL​) | V | 960 | User-specified AC voltage. | 
DC-Link Voltage (Vdc​) | V | 1536 | 1.6×VLL​ (Calculated). | 
Switching Frequency (fsw​) | kHz | 2.5 | Typical value for high-power IGBT converters (2−4 kHz). | 
DC Link Capacitance (Cdc​) | mF | 75 | Estimated for ∼7 ms holdup time and 5% voltage ripple. | 
Rectifier Side Inductance (Lr​) | mH | 0.18 | External coupling inductor for Rotor Side Converter (≈7.5% pu). | 
Inverter Side Inductance (L1​) | mH | 0.12 | Converter side inductor of the Grid LCL filter. | 
Filter Capacitor (Cf​) | μF | 125 | Estimated for 5% reactive power absorption at VLL​. | 
Grid Side Inductance (L2​) | mH | 0.06 | Grid side inductor of the Grid LCL filter. | 
Filter Resistance (Rd​) | Ω | 1−3 | Estimate for passive damping of the LCL filter resonance. | 
Dimensions (L×W×H) | mm | 2000×1000×2200 | Typical dimensions for a 1.25 MW liquid-cooled cabinet. | 
Weight | kg | 1500−3500 | Typical weight range for a 1.25 MW VSC cabinet. | 
Auxiliary Supply | V | 400 VAC​ | Standard 3-phase supply for cooling/auxiliary motors and pumps. | 

## Slide 9: 6.Next Step
Cristina Vergara
Complete the Simscape drivetrain diagram and add all parameters.
Run the first full simulation and compare it with the MATLAB results.
3D modeling (Fusion 360) of components

## Slide 10: Bibliography
11/18/2025
Cristina Vergara
9
MathWorks. Simscape Electrical Documentation. https://www.mathworks.com/help/sps/ Access Date – 06/11/2025
MathWorks. Asynchronous Machine (Wound Rotor) – Simscape Electrical. https://www.mathworks.com/help/sps/ref/asynchronousmachine.html Access Date – 06/11/2025
MathWorks. DFIG Wind Turbine Examples (Simscape). https://www.mathworks.com/help/sps/ug/wind-turbine-modeling.html Access Date – 06/11/2025
MathWorks. Wind Turbine Induction Generator Models. https://www.mathworks.com/help/sps/powersys/ref/dfigwindturbine.html Access Date – 06/11/2025