## Slide 1
Weekly report: Electrical Drivetrain
Week number: 9
Date: 11/25/2025
Supervisor: Prof. Dr.-Ing. Saiju
Group members: Aiswarya Vijayan, Vishranti Shivajirao Patil , Girish Mahadeo Padalkar, Cristina Milene Vergara Hernandez

## Slide 2: List of contents
Cristina Vergara
Electrical Drive Train/ Optimus Syria
Implement MATLAB model of the DFIG
Generate characteristic curves for DFIG
Begin building the Simscape model for all drivetrain components
Cable Calculations

## Slide 3: Cable cross-section calculation
Cristina Vergara
Determine operating currents
  Stator: 3440 A (5.72 MVA at 960 V)
  Converter AC (rotor & grid): 900 A (1.5 MVA at 960 V)
  MV side: 165 A (5.72 MVA at 20 kV)
Determine required cable ampacity
  Apply derating factors (from ABB/IEC tables):
  Ambient temperature factor: 0.95 (assumption)
  Grouping factor: 1.0 (assumption)
3. Required ampacity per cable
4. Compare to ABB XLPE cable CCC tables Select the cable cross-section whose CCC × k ≥ operating current.

## Slide 4: Cable cross-section calculation
Cristina Vergara

## Slide 5: Cable cross-section calculation
Cristina Vergara

## Slide 6: Final Cable Selection for the Drivetrain
Cristina Vergara
1. Stator → LV Transformer (960 V, 3.44 kA)
Required CCC per phase after derating: ≈ 1480 A
ABB 630 mm² Al LV cable: CCC ≈ 780 A → derated ≈ 589 A
Practical OEM solution (short nacelle run): 3 × (1×630 mm² Al) per phase → Total: 9 single-core LV XLPE cables
2. Rotor Windings → Rotor-Side Converter (900 A)
  Required CCC after derating: ≈ 1190 A
  One 630 mm² Al cable is acceptable for short runs (converter inside nacelle) → 1 × (1×630 mm² Al) per phase
3. Grid-Side Converter → LV Transformer (900 A)
  Same current as rotor-side converter
  Same cable type chosen for symmetry → 1 × (1×630 mm² Al) per phase
4. MV Transformer → 20 kV Switchgear (165 A)
  ABB NA2XS2Y 1×95 mm² Al (12/20 kV): CCC ≈ 260 A → derated ≈ 196 A
  Required current: 165 A < 196 A → 1 × (1×95 mm² Al, 12/20 kV)

## Slide 7: Torque-Speed Characteristic
Cristina Vergara
Torque is positive below synchronous speed
Zero torque ~1000 rpm
Negative torque above synchronous speed → generator region
Curve shape matches theoretical DFIG characteristics

## Slide 8: Stator Current vs Rotor Speed
Cristina Vergara
Stator current is lowest near synchronous speed
Higher slip → higher stator current
Symmetrical behaviour indicates correct model implementation

## Slide 9: Mechanical Power vs Rotor Speed
Cristina Vergara
Mechanical power peaks at low speed (motor side)
Zero crossing at synchronous speed
Becomes negative in generator range (expected)
Confirms correct energy flow direction

## Slide 10: Mechanical Power vs Rotor Speed
Cristina Vergara
Torque vs. Speed: Constant-power control → torque decreases as speed increases.
Power Split: Stator delivers most power; converter only handles slip power (~20–25%).
Converter Current: Increases with slip; reaches rated limit near ±0.3 slip.
Overall: Confirms correct DFIG behaviour—small converter handles variable-speed control while stator feeds main power to grid.

## Slide 11: 6.Next Step
Cristina Vergara
Complete the Simscape drivetrain diagram and add all parameters.
3D modeling (Fusion 360) of components

## Slide 12: Bibliography
11/25/2025
Cristina Vergara
9
MathWorks. Simscape Electrical Documentation. https://www.mathworks.com/help/sps/ Access Date – 06/11/2025
MathWorks. Asynchronous Machine (Wound Rotor) – Simscape Electrical. https://www.mathworks.com/help/sps/ref/asynchronousmachine.html Access Date – 06/11/2025
MathWorks. DFIG Wind Turbine Examples (Simscape). https://www.mathworks.com/help/sps/ug/wind-turbine-modeling.html Access Date – 06/11/2025
MathWorks. Wind Turbine Induction Generator Models. https://www.mathworks.com/help/sps/powersys/ref/dfigwindturbine.html Access Date – 06/11/2025
XLPE%20Cable%20Systems%20Users%20Guide (003)