## Slide 1
5th Week Presentation
Date:28 Oct. 2025

## Slide 2
Weekly report: Team Grid code Development
Week number: 5
Date: 24/10/2025
Supervisor: Prof. Dr. -Ing. Rajesh Saiju
Presented by: Vijay Bogala / Josef Remberger

## Slide 3: List of contents
Milestones
Additional characterstic parameters
Detailed guidelines

## Slide 4: 1. Milestones

## Slide 5: 2. Additional characterstic parameters
Voltage:
  Deviation limit: ±3%
DC injection: <0.25 of
Short circuit power
[2] PETE, 2022
Voltage | Power limit (MW)
Distribution network i.e. Medium voltage @ 20 kV | 10
Transmission network i.e. High voltage @ 66 kV | 40
Transmission network i.e. High voltage @ 230 kV | 100

## Slide 6: 2. Additional characterstic parameters
Voltage flicker:
  PETE: IEEE 519-1992 “maximum borderline of irritation curve“ or the relevant standard
  P_st <1.0 , P_lt <0.7 [2] PETE, 2022
  Which is outdated
  Better: IEC 61400-21-1:2019 & VDE FNN AR N 4110:2019
  P_st <0.35 , P_lt <0.25 [1] VDE, 2019 [4] IEC, 2019
Phase imbalance:
  voltage deviations among phases<2% [2] PETE, 2022
Power factor: [2] PETE, 2022
  >0.98, leading or lagging
  for special cases, deviations might be allowed
[1], [2], [4].

## Slide 7: 3. Necessary guidelines
PETE i.e. Syria grid code publisher
  Rules and Conditions for Connecting Renewable Energy Projects to the Transmission and Distribution Networks: 2022
  Transmission Grid Code: 2014
VDE FNN
  VDE-AR-N 4110: 2023-09 i.e. Medium voltage
  VDE-AR-N 4120:2017-05 i.e. High voltage
IEC
  IEC 61400-21-1:2019 Measurement and assessment of electrical characteristics - Wind turbines
  IEC 61400-21-2:2023 Measurement and assessment of electrical characteristics - Wind turbines
[1], [2]….

## Slide 8: 3. Necessary guidelines
IEC
  IEC TR 61400-21-3:2019 Wind turbine Harmonic model and its application
  IEC TS 61400-21-4:2025 Wind turbine components and subsystems
  IEC 61400-27-1:2020 Electrical simulation models - Generic models
  IEC 61400-27-2:2020 Electrical simulation models - Model validation
[1], [2]….

## Slide 9: Bibliography – Grid Code Development
[1] “Summary of the draft. VDE-AR-N 4110:2023-09” VDE FNN, 2023. Accessed: Oct. 27, 2025. [Online]. Available: https://eepublicdownloads.entsoe.eu/clean-documents/cnc-active-library/Germany/summary-draft-4110-en.pdf
[2] “Syrian Arab Republic Ministry of Electricity Public Establishment for Transmission & Distribution of Electricity Interconnection Roles Rules and Conditions for Connecting Renewable Energy Projects to the Transmission and Distribution Networks,” 2022. Accessed: Oct. 27, 2025. [Online]. Available: https://tde.gov.sy/sites/default/files/2025-07/Rules%20and%20Conditions%20for%20Connecting%20Renewable%20Energy%20Projects%20to%20the%20Transmission%20and%20Distribution%20Networks.pdf
[3] "IEEE Recommended Practices and Requirements for Harmonic Control in Electrical Power Systems," in IEEE Std 519-1992 , vol., no., pp.1-112, 9 April 1993, doi: 10.1109/IEEESTD.1993.114370
[4] "IEC 61400-21-1:2019 Measurement and assessment of electrical characteristics - Wind turbines” IEC, 2019. Accessed: Oct. 27, 2025. [Online]. https://webstore.iec.ch/en/publication/29528.