## Slide 1: Weekly report: Storage System
6th week – 7th Presentation
Date: 04/11/2025
Supervisor: Dr. Laurence Alhrshy
Group members: Mohamed Ahmed
Mohamed Ahmed
04/11/2025
Storage System Team/ Optimus Syria
Notes: `

## Slide 2
Content
Major Factors in Battery ESS Dimensioning​
Battery Sizing ​
Next Presentation : Supplier
References
Mohamed Ahmed
04/11/2025
Storage System Team/ Optimus Syria

## Slide 3: The Major Factors in Dimensioning a Battery Energy Storage System
Battery Type: We have chosen Lithium-ion
Energy Storage Capacity
  The total amount of energy the battery can store, usually measured in kilowatt-hours (kWh) or megawatt-hours (MWh).
  This determines how much energy the system can store from the wind turbine.
  Capacity (kWh)=Power (kW)×Time (h)
Power Output (Discharge Power)
  The maximum rate at which the battery can deliver energy.
Mohamed Ahmed
Storage System Team/ Optimus Syria
Energy (kWh)
Time (h)
Power Output (kW) =
04/11/2025

## Slide 4: The Major Factors in Dimensioning a Battery Energy Storage System
Round-Trip Efficiency
  Indicates the efficiency of the storage system, accounting for energy losses during charging and discharging.
Depth of Discharge (DoD)
  The percentage of the battery's capacity that is used relative to the total capacity.
  Higher DoD typically results in shorter battery life.
Mohamed Ahmed
Storage System Team/ Optimus Syria
​Energy Out (kWh)
Energy In (kWh)
Round-Trip Efficiency (%) =
× 100
Energy Used (kWh)
Total Capacity (kWh)
DoD (%) =
× 100
04/11/2025

## Slide 5: The Major Factors in Dimensioning a Battery Energy Storage System
Mohamed Ahmed
Storage System Team/ Optimus Syria
State of Charge (SoC)
  The current level of energy stored in the battery, often represented as a percentage of total capacity.
  Important for controlling the charge-discharge cycles and optimizing system performance.
Response Time
  How quickly the battery can respond to energy demands or store excess energy.
  Critical for grid stability and managing fluctuating energy generation
  Response Time = Time to Full Power Output
04/11/2025

## Slide 6: The Major Factors in Dimensioning a Battery Energy Storage System
Mohamed Ahmed
Storage System Team/ Optimus Syria
Energy Management System (EMS)
  The control system that manages when and how the battery charges and discharges.
  Ensures optimal use of energy from the wind turbine, maintains battery health, and integrates with the grid.
Location and Environmental Conditions
  Temperature and humidity can affect battery performance.
Cost (Capital and Operating)
  Includes the initial cost of the battery, installation, and maintenance costs over its lifetime.
  Critical for economic feasibility of wind energy storage projects.
  Levelized Cost of Storage (LCOS):
∑ Total Lifetime Costs
∑ Total Energy Discharged (kWh)
LCOS =
04/11/2025

## Slide 7: Dimensioning of the Storage System
Mohamed Ahmed
Storage System Team/ Optimus Syria
Assumptions
  A 5 MW rated power of the wind turbine.
  40 % wind turbine capacity factor.
  4 Hours desired storage time.
  90 % round-trip efficiency.
  6% curtailment rate of wind energy in Qattienh.
04/11/2025

## Slide 8: Dimensioning of the Storage System
Mohamed Ahmed
4/11/2025
Storage System Team/ Optimus Syria
Calculation of the Annual Energy Generated by the Wind Turbine
Annual Energy (E) = Rated Power × Capacity Factor × Hours in a Year
Hours in a Year = 365 days × 24 hours/day = 8760 hours
E = 5 MW × 0.40 × 8760 hours = 17,520 MWh
Adjust for Qattienh Wind Energy Curtailment rate
Effective Annual Energy = E × (1 – Curtailment Rate)
Curtailment Rate = 0.06
Effective Annual Energy = 17,520 × (1 – 0.06) = 16,468.8 MWh
Effective Daily Energy =​
16,468.8 MWh
365
≈ 45.12 MWh

## Slide 9: Dimensioning of the Storage System
Mohamed Ahmed
4/11/2025
Storage System Team/ Optimus Syria
Calculation of Battery Energy Capacity
Calculation of Battery Power Capacity ( Power Discharge )
  Power capacity of the battery can be determined from the storage time and the energy capacity
Effective Daily Energy
Round-Trip Efficiency
Battery Energy Capacity =
45.12 MWh
0.9
=
Battery Energy Capacity
Storage Time
Battery Power Capacity =
50.13 MWh
4
=
≈ 12.53 MW

## Slide 10: Next Presentation : Supplier
Mohamed Ahmed
4/11/2025
Storage System Team/ Optimus Syria
  In the next presentation, we will discuss the supplier of the Battery Energy Storage System used in our project in Syria.
  We will briefly present the selected company, its product specifications, and why it was chosen for the Optimus Syria storage system.
  This part will highlight the importance of selecting reliable suppliers to ensure system efficiency and long-term performance.

## Slide 11: References
https://www.osti.gov/biblio/1847886
https://www.nrel.gov/docs/fy21osti/78347.pdf
Mohamed Ahmed
4/11/2025
Storage System Team/ Optimus Syria