## Slide 1
Weekly report: Grid Code Development
Week number: 11
Date: 09/12/2025
Supervisor: Prof. Ing. Saiju
Presented by: Josef Remberger / Vijay Simha Reddy Bogala

## Slide 2: List of contents
PowerFactory Results
  PowerFlow
  Short Circuit
  LVRT
  HVRT
Conclusion
Josef Remberger

## Slide 3: 1-i. PowerFlow
Number of turbines: 4
Power at the PCC (Qattinah Substation): 19,57MW
[1]
Josef Remberger

## Slide 4: 1-ii. Short Circuit
Complete 3-Phase short circuit at PCC
Josef Remberger
[1]

## Slide 5: 1-iii. LVRT
V_grid = 0 %, time = 100 ms
Josef Remberger
[1]

## Slide 6: 1-iii. LVRT
V_grid = 20 %, time = 500 ms
Josef Remberger
[1]

## Slide 7: 1-iii. LVRT
V_grid = 80 %, time = 1000 ms
Josef Remberger
[1]

## Slide 8: 1-iv. LVRT
V_grid = 90 %, time = 15000 ms
Josef Remberger
[1]

## Slide 9: 1-iv. HVRT
V_grid = 125 %, time = 100 ms
Josef Remberger
[1]

## Slide 10: 1-iv. HVRT
V_grid = 120 %, time = 5000 ms -> turbines are disconnected due to inadequate protection settings in the turbine controller
Josef Remberger
[1]

## Slide 11: 2. Conclusion
Grid Code compliance for our turbine with the current protection devices excluded the 120% HVRT✓
  -> Adjustments must be made to the controller settings in PowerFactory
Josef Remberger

## Slide 12: Bibliography – Grid Code Development
[1] Created with PowerFactory / DigSilent